## Sayfa1
FORM NO : LAB.FRM.31 / 06.03.2015 / Rev. 0
| BİRİM : SERTİFİKASYON |  | DÖNEM: | SAYFA NO:
TEMPERATURE RESISTANCE TEST REPORT
Date | 2015-02-17
Report Code | 170213.ALU.01
Product | ALUAFS.70
Diameter | Ø127 mm
Length | 1 m
RESULTS
Time(min) | Inlet Temperature (˚C) | Outlet Temperature (˚C) | Photograph No. | Evaluation
0 | - | - | 1-2 | The sample was tested at an inlet temperature of 150ºC for 4 hours and photographed at the end of the test. At the end of the 4 hour test, no tears, flaps or ruptures were observed.
60 | 155 | 119
120 | 154 | 118
180 | 143 | 114
240 | 147 | 115
PHOTOGRAPHS
1 |  |  |  | 2