## Sayfa1
FORM NO : LAB.FRM.31 / 06.03.2015 / Rev. 0
|  | BİRİM : SERTİFİKASYON |  | DÖNEM: |  | SAYFA NO:
TEMPERATURE RESISTANCE TEST REPORT
| Date | 2015-08-26
| Report Code | 260815.POLY.01
| Product | POLYAFS
| Diameter | Ø127 mm
| Length | 1 m
RESULTS
| Time(min) | Inlet Temperature (˚C) | Outlet Temperature (˚C) | Photograph No. | Evaluation
| 0 | - | - | 1 | The sample was tested at an inlet temperature of 120ºC for 4 hours. The sample was photographed hourly. At the end of the 4 hour test no tears or ruptures were observed.
| 60 | 122 | 97 | 2
| 120 | 122 | 97 | 3
| 180 | 121 | 95 | 4
| 240 | 122 | 96 | 5
PHOTOGRAPHS
1
2
3
4
| 9 |  |  | 10
| 11 |  |  | 12