## Sayfa1
FORM NO : LAB.FRM.31 / 06.03.2015 / Rev. 0
| BİRİM : SERTİFİKASYON |  | DÖNEM: 2015 | SAYFA NO:
TEMPERATURE RESISTANCE TEST REPORT
Date | 2015-04-10
Report Code | 100415.PVCAFS.01
Product | PVCAFS BLUE
Diameter | Ø127 mm
Length | 1 m
RESULTS
Time(min) | Inlet Temperature (˚C) | Outlet Temperature (˚C) | Photograph No. | Evaluation
0 | - | - | 1 | The sample was tested at an inlet temperature of 80ºC for 4 hours and photographed hourly. At the end of the 4 hour test no tears or ruptures were observed.
60 | 79 | 65 | 2
120 | 80 | 65 | 3
180 | 80 | 64 | 4
240 | 80 | 65 | 5
PHOTOGRAPHS
1
3
4
2
5